## SCADA Checklist
ANNEX Z.1 - SCADA CHECKLIST PRIOR TO ERF APPLICATION
Completion Date:
PLANT DETAILS
Region | District | Site Name |  | Voltage Rating | Barangay |  | City |  | Province
PRELIMINARY DOCUMENTS REQUIRED
DOCUMENT: | [5 empty] | Submitted: | Plant Remarks: |  | NGCP Remarks:
PLANT SLD (ASBUILT & SIMPLIFIED)
SCADA ARCHITECTURE
TELECOM ARCHITECTURE
OTHERS: (Please specify)
PLANT TO MASTER STATION LINK REQUIREMENTS
[6 empty] | Complied: | Plant Remarks: |  | NGCP Remarks:
Channel: LRCC, BLRCC & ACC |  |  | TCP/IP connection
Protocol: DNP3 |  |  | Integrity Poll - 5 minutes
Class 1, 2, 3 - 500 ms - 1 sec
Time Synchronization - 5 minutes
Sequence of Events |  |  | Status Indication
GPS Time Synchronization |  |  | via DNP3.0/NTP/IRIG-B/PTP
Others: (Please specify)
COMPLETION OF SCADA MONITORING BASED ON THE PROVIDED INPUT/OUTPUT LIST
| AS LOAD | - Monitoring of Outgoing Line down to Main Transformer
| AS GENERATION |  | - Complete monitoring based on the I/O List provided by NGCP
DATA TYPE: |  | Required activity |  |  | Initial Testing: | Final Testing: | Plant Remarks: |  | NGCP Remarks:
Analog |  | Validation of Analog Injected Values
Status |  | Simulation of indication
Actual testing
Local Control (if required)
Remote Control w/ prioritization (if required)
Others: (Please specify)
STATEMENT OF AGREEMENT
Submission of this form means concurrence to the following: (1) we agree that above requirements should be complied prior to application of Energization Request Form (ERF) (2) Compliance to the above requirements shall be validated and approved by NGCP. (3) NGCP shall not be limited by the above requirements and is authorized to revise any of the above requirement or this form anytime if necessary to satisfy new grid requirements.
| Submitted by (Plant): | [5 empty] | Approved by(NGCP):
| Name and Signature / Date | [5 empty] | Name and Signature / Date